## Sheet1
|  | Domain |  | Sub-Domain | Requirement
5 | 5.1 | FR 1 – Identification and authentication control | 5.1-SL 1 | Purpose and SL-C(IAC) descriptions | Identify and authenticate all users (humans, software processes and devices) by mechanisms that protect against casual or coincidental access by unauthenticated entities.
5 | 5.1 | FR 1 – Identification and authentication control | 5.1-SL 2 | Purpose and SL-C(IAC) descriptions | Identify and authenticate all users (humans, software processes and devices) by mechanisms that protect against intentional unauthenticated access by entities using simple means with low resources, generic skills and low motivation.
5 | 5.1 | FR 1 – Identification and authentication control | 5.1-SL 3 | Purpose and SL-C(IAC) descriptions | Identify and authenticate all users (humans, software processes and devices) by mechanisms that protect against intentional unauthenticated access by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation.
5 | 5.1 | FR 1 – Identification and authentication control | 5.1-SL 4 | Purpose and SL-C(IAC) descriptions | Identify and authenticate all users (humans, software processes and devices) by mechanisms that protect against intentional unauthenticated access by entities using sophisticated means with extended resources, IACS specific skills and high motivation.
5 | 5.3 | FR 1 – Identification and authentication control | 5.3.1 | CR 1.1 – Human user identification and authentication | Components shall provide the capability to identify and authenticate all human users according to ISA‑62443‑3‑3 [11] SR 1.1 on all interfaces capable of human user access. This capability shall enforce such identification and authentication on all interfaces that provide human user access to the component to support segregation of duties and least privilege in accordance with applicable security policies and procedures. This capability may be provided locally by the component or by integration into a system level identification and authentication system.
5 | 5.3 | FR 1 – Identification and authentication control | 5.3.3-1 | CR 1.1 – Human user identification and authentication | Components shall provide the capability to uniquely identify and authenticate all human users.
5 | 5.3 | FR 1 – Identification and authentication control | 5.3.3-2 | CR 1.1 – Human user identification and authentication | Components shall provide the capability to employ multifactor authentication for all human user access to the component.
5 | 5.3 | FR 1 – Identification and authentication control | 5.3.4-1 | CR 1.1 – Human user identification and authentication | Requirements for the security level that relates to SL-C(IAC,component) 1: CR 1.1
5 | 5.3 | FR 1 – Identification and authentication control | 5.3.4-2 | CR 1.1 – Human user identification and authentication | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.1 (1)
5 | 5.3 | FR 1 – Identification and authentication control | 5.3.4-3 | CR 1.1 – Human user identification and authentication | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.1 (1) (2)
5 | 5.3 | FR 1 – Identification and authentication control | 5.3.4-4 | CR 1.1 – Human user identification and authentication | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.1 (1) (2)
5 | 5.4 | FR 1 – Identification and authentication control | 5.4.1 | CR 1.2 – Software process and device identification and authentication | Components shall provide the capability to identify itself and authenticate to any other component (software application, embedded devices, host devices and network devices), according to ISA‑62443‑3‑3 [11] SR1.2. If the component, as in the case of an application, is running in the context of a human user, in addition, the identification and authentication of the human user according to ISA‑62443‑3‑3 [11] SR1.1 may be part of the component identification and authentication process towards the other components.
5 | 5.4 | FR 1 – Identification and authentication control | 5.4.3-1 | CR 1.2 – Software process and device identification and authentication | Components shall provide the capability to uniquely identify and authenticate itself to any other component.
5 | 5.4 | FR 1 – Identification and authentication control | 5.4.4-1 | CR 1.2 – Software process and device identification and authentication | Requirements for the security level that relates to SL-C(IAC,component) 1: Not Selected
5 | 5.4 | FR 1 – Identification and authentication control | 5.4.4-2 | CR 1.2 – Software process and device identification and authentication | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.2
5 | 5.4 | FR 1 – Identification and authentication control | 5.4.4-3 | CR 1.2 – Software process and device identification and authentication | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.2 (1)
5 | 5.4 | FR 1 – Identification and authentication control | 5.4.4-4 | CR 1.2 – Software process and device identification and authentication | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.2 (1)
5 | 5.5 | FR 1 – Identification and authentication control | 5.5.1 | CR 1.3 – Account management | Components shall provide the capability to support the management of all accounts directly or integrated into a system that manages accounts according to ISA‑62443‑3‑3 [11] SR 1.3.
5 | 5.5 | FR 1 – Identification and authentication control | 5.5.4-1 | CR 1.3 – Account management | Requirements for the security level that relates to SL-C(IAC,component) 1: CR 1.3
5 | 5.5 | FR 1 – Identification and authentication control | 5.5.4-2 | CR 1.3 – Account management | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.3
5 | 5.5 | FR 1 – Identification and authentication control | 5.5.4-3 | CR 1.3 – Account management | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.3
5 | 5.5 | FR 1 – Identification and authentication control | 5.5.4-4 | CR 1.3 – Account management | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.3
5 | 5.6 | FR 1 – Identification and authentication control | 5.6.1 | CR 1.4 – Identifier management | Components shall provide the capability to integrate into a system that supports the management of identifiers and/or provide the capability to support the management of identifiers directly according to ISA‑62443‑3‑3 [11] SR 1.4.
5 | 5.6 | FR 1 – Identification and authentication control | 5.6.4-1 | CR 1.4 – Identifier management | Requirements for the security level that relates to SL-C(IAC,component) 1: CR 1.4
5 | 5.6 | FR 1 – Identification and authentication control | 5.6.4-2 | CR 1.4 – Identifier management | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.4
5 | 5.6 | FR 1 – Identification and authentication control | 5.6.4-3 | CR 1.4 – Identifier management | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.4
5 | 5.6 | FR 1 – Identification and authentication control | 5.6.4-4 | CR 1.4 – Identifier management | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.4
5 | 5.7 | FR 1 – Identification and authentication control | 5.7.1 | CR 1.5 – Authenticator management | Components shall provide the capability to: a) support the use of initial authenticator content; b) support the recognition of changes to default authenticators made at installation time; c) function properly with periodic authenticator change/refresh operation; and d) protect authenticators from unauthorized disclosure and modification when stored, used and transmitted.
5 | 5.7 | FR 1 – Identification and authentication control | 5.7.3-1 | CR 1.5 – Authenticator management | The authenticators on which the component rely shall be protected via hardware mechanisms. Note: Examples of hardware authentication include: Password protected memory, OTP memory, hardware data integrity checks, and device security boot mechanism.
5 | 5.7 | FR 1 – Identification and authentication control | 5.7.4-1 | CR 1.5 – Authenticator management | Requirements for the security level that relates to SL-C(IAC,component) 1: CR 1.5
5 | 5.7 | FR 1 – Identification and authentication control | 5.7.4-2 | CR 1.5 – Authenticator management | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.5
5 | 5.7 | FR 1 – Identification and authentication control | 5.7.4-3 | CR 1.5 – Authenticator management | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.5 (1)
5 | 5.7 | FR 1 – Identification and authentication control | 5.7.4-4 | CR 1.5 – Authenticator management | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.5 (1)
5 | 5.8 | FR 1 – Identification and authentication control |  | CR 1.6 – Wireless access management | The wireless access management requirements are network-component-specific and can be located as requirements for network-components in Clause 15.
5 | 5.9 | FR 1 – Identification and authentication control | 5.9.1 | CR 1.7 – Strength of password-based authentication | For components that utilize password-based authentication, those components shall provide or integrate into a system that provides the capability to enforce configurable password strength according to internationally recognized and proven password guidelines .
5 | 5.9 | FR 1 – Identification and authentication control | 5.9.3-1 | CR 1.7 – Strength of password-based authentication | Components shall provide, or integrate into a system that provides, the capability to protect against any given human user account from reusing a password for a configurable number of generations. In addition, the component shall provide the capability to enforce password minimum and maximum lifetime restrictions for human users. These capabilities shall conform to commonly accepted security industry practices. NOTE The component should provide the capability to prompt the user to change their password upon a configurable time prior to expiration.
5 | 5.9 | FR 1 – Identification and authentication control | 5.9.3-2 | CR 1.7 – Strength of password-based authentication | Components shall provide, or integrate into a system that provides, the capability to enforce password minimum and maximum lifetime restrictions for all users.
5 | 5.9 | FR 1 – Identification and authentication control | 5.9.4-1 | CR 1.7 – Strength of password-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 1: CR 1.7
5 | 5.9 | FR 1 – Identification and authentication control | 5.9.4-2 | CR 1.7 – Strength of password-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.7
5 | 5.9 | FR 1 – Identification and authentication control | 5.9.4-3 | CR 1.7 – Strength of password-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.7 (1)
5 | 5.9 | FR 1 – Identification and authentication control | 5.9.4-4 | CR 1.7 – Strength of password-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.7 (1) (2)
5 | 5.10 | FR 1 – Identification and authentication control | 5.10.1 | CR 1.8 – Public key infrastructure certificates | When public key infrastructure (PKI) is utilized, the component shall provide or integrate into a system that provides the capability to interact and operate in accordance with ISA‑62443‑3‑3 [11] SR1.8.
5 | 5.10 | FR 1 – Identification and authentication control | 5.10.4-1 | CR 1.8 – Public key infrastructure certificates | Requirements for the security level that relates to SL-C(IAC,component) 1: Not Selected
5 | 5.10 | FR 1 – Identification and authentication control | 5.10.4-2 | CR 1.8 – Public key infrastructure certificates | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.8
5 | 5.10 | FR 1 – Identification and authentication control | 5.10.4-3 | CR 1.8 – Public key infrastructure certificates | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.8
5 | 5.10 | FR 1 – Identification and authentication control | 5.10.4-4 | CR 1.8 – Public key infrastructure certificates | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.8
5 | 5.11 | FR 1 – Identification and authentication control | 5.11.1 | CR 1.9 – Strength of public key-based authentication | For components that utilize public-key-based authentication, those components shall provide directly or integrate into a system that provides the capability within the same IACS environment to: a) validate certificates by checking the validity of the signature of a given certificate; b) validate the certificate chain or, in the case of self-signed certificates, by deploying leaf certificates to all hosts that communicate with the subject to which the certificate is issued; c) validate certificates by checking a given certificate’s revocation status; d) establish user (human, software process or device) control of the corresponding private key; e) map the authenticated identity to a user (human, software process or device); and f) ensure that the algorithms and keys used for the public key authentication comply with 8.5 CR 4.3 – Use of cryptography.
5 | 5.11 | FR 1 – Identification and authentication control | 5.11.3-1 | CR 1.9 – Strength of public key-based authentication | Components shall provide the capability to protect critical, long-lived private keys via hardware mechanisms.
5 | 5.11 | FR 1 – Identification and authentication control | 5.11.4-1 | CR 1.9 – Strength of public key-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 1: Not Selected
5 | 5.11 | FR 1 – Identification and authentication control | 5.11.4-2 | CR 1.9 – Strength of public key-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.9
5 | 5.11 | FR 1 – Identification and authentication control | 5.11.4-3 | CR 1.9 – Strength of public key-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.9 (1)
5 | 5.11 | FR 1 – Identification and authentication control | 5.11.4-4 | CR 1.9 – Strength of public key-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.9 (1)
5 | 5.12 | FR 1 – Identification and authentication control | 5.12.1 | CR 1.10 – Authenticator feedback | When a component provides an authentication capability the component shall provide the capability to obscure feedback of authenticator information during the authentication process.
5 | 5.12 | FR 1 – Identification and authentication control | 5.12.4-1 | CR 1.10 – Authenticator feedback | Requirements for the security level that relates to SL-C(IAC,component) 1: CR 1.10
5 | 5.12 | FR 1 – Identification and authentication control | 5.12.4-2 | CR 1.10 – Authenticator feedback | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.10
5 | 5.12 | FR 1 – Identification and authentication control | 5.12.4-3 | CR 1.10 – Authenticator feedback | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.10
5 | 5.12 | FR 1 – Identification and authentication control | 5.12.4-4 | CR 1.10 – Authenticator feedback | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.10
5 | 5.13 | FR 1 – Identification and authentication control | 5.13.1 | CR 1.11 – Unsuccessful login attempts | When a component provides an authentication capability the component shall provide the capability to: a) enforce a limit of a configurable number of consecutive invalid access attempts by any user (human, software process or device) during a configurable time period; and b) deny access for a specified period of time or until unlocked by an administrator when this limit has been reached. Note: An administrator may unlock an account prior to the expiration of the timeout period.
5 | 5.13 | FR 1 – Identification and authentication control | 5.13.4-1 | CR 1.11 – Unsuccessful login attempts | Requirements for the security level that relates to SL-C(IAC,component) 1: CR 1.11
5 | 5.13 | FR 1 – Identification and authentication control | 5.13.4-2 | CR 1.11 – Unsuccessful login attempts | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.11
5 | 5.13 | FR 1 – Identification and authentication control | 5.13.4-3 | CR 1.11 – Unsuccessful login attempts | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.11
5 | 5.13 | FR 1 – Identification and authentication control | 5.13.4-4 | CR 1.11 – Unsuccessful login attempts | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.11
5 | 5.14 | FR 1 – Identification and authentication control | 5.14.1 | CR 1.12 – System use notification | When a component provides local human user access/HMI, it shall provide the capability to display a system use notification message before authenticating. The system use notification message shall be configurable by authorized personnel.
5 | 5.14 | FR 1 – Identification and authentication control | 5.14.4-1 | CR 1.12 – System use notification | Requirements for the security level that relates to SL-C(IAC,component) 1: CR 1.12
5 | 5.14 | FR 1 – Identification and authentication control | 5.14.4-2 | CR 1.12 – System use notification | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.12
5 | 5.14 | FR 1 – Identification and authentication control | 5.14.4-3 | CR 1.12 – System use notification | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.12
5 | 5.14 | FR 1 – Identification and authentication control | 5.14.4-4 | CR 1.12 – System use notification | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.12
5 | 5.15 | FR 1 – Identification and authentication control |  | CR 1.13 – Access via untrusted networks | The access via untrusted networks requirements are component-specific and can be located as requirements for each specific component type in Clauses 12 through 15.
5 | 5.16 | FR 1 – Identification and authentication control | 5.16.1 | CR 1.14 – Strength of symmetric key-based authentication | For components that utilize symmetric keys, the component shall provide the capability to: a) establish the mutual trust using the symmetric key; b) store securely the shared secret (the authentication is valid as long as the shared secret remains secret); c) restrict access to the shared secret; and d) ensure that the algorithms and keys used for the symmetric key authentication comply with CR 4.3 – Use of cryptography Subclause 8.5.
5 | 5.16 | FR 1 – Identification and authentication control | 5.16.3-1 | CR 1.14 – Strength of symmetric key-based authentication | Components shall provide the capability to protect critical, long lived symmetric keys via hardware mechanisms.
5 | 5.16 | FR 1 – Identification and authentication control | 5.16.4-1 | CR 1.14 – Strength of symmetric key-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 1: Not selected
5 | 5.16 | FR 1 – Identification and authentication control | 5.16.4-2 | CR 1.14 – Strength of symmetric key-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 2: CR 1.14
5 | 5.16 | FR 1 – Identification and authentication control | 5.16.4-3 | CR 1.14 – Strength of symmetric key-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 3: CR 1.14 (1)
5 | 5.16 | FR 1 – Identification and authentication control | 5.16.4-4 | CR 1.14 – Strength of symmetric key-based authentication | Requirements for the security level that relates to SL-C(IAC,component) 4: CR 1.14 (1)
6 | 6.1 | FR 2 – Use control | 6.1-SL 1 | Purpose and SL-C(UC) descriptions | Restrict use of the IACS according to specified privileges to protect against casual or coincidental misuse.
6 | 6.1 | FR 2 – Use control | 6.1-SL 2 | Purpose and SL-C(UC) descriptions | Restrict use of the IACS according to specified privileges to protect against circumvention by entities using simple means with low resources, generic skills and low motivation.
6 | 6.1 | FR 2 – Use control | 6.1-SL 3 | Purpose and SL-C(UC) descriptions | Restrict use of the IACS according to specified privileges to protect against circumvention by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation.
6 | 6.1 | FR 2 – Use control | 6.1-SL 4 | Purpose and SL-C(UC) descriptions | Restrict use of the IACS according to specified privileges to protect against circumvention by entities using sophisticated means with extended resources, IACS specific skills and high motivation.
6 | 6.3 | FR 2 – Use control | 6.3.1 | CR 2.1 – Authorization enforcement | Components shall provide an authorization enforcement mechanism for all identified and authenticated users based on their assigned responsibilities.
6 | 6.3 | FR 2 – Use control | 6.3.3-1 | CR 2.1 – Authorization enforcement | Components shall provide an authorization enforcement mechanism for all users based on their assigned responsibilities and least privilege.
6 | 6.3 | FR 2 – Use control | 6.3.3-2 | CR 2.1 – Authorization enforcement | Components shall, directly or through a compensating security mechanism, provide for an authorized role to define and modify the mapping of permissions to roles for all human users. NOTE 1 Roles should not be limited to fixed nested hierarchies in which a higher level role is a super set of a lesser privileged role. For example, a system administrator should not necessarily encompass operator privileges. NOTE 2 This RE should be applicable to software processes and devices as well.
6 | 6.3 | FR 2 – Use control | 6.3.3-3 | CR 2.1 – Authorization enforcement | Components shall support a supervisor manual override for a configurable time or sequence of events. NOTE Implementation of a controlled, audited and manual override of automated mechanisms in the event of emergencies or other serious events is often needed. This allows a supervisor to enable an operator to quickly react to unusual conditions without closing the current session and establishing a new session as a higher privilege human user.
6 | 6.3 | FR 2 – Use control | 6.3.3-4 | CR 2.1 – Authorization enforcement | Components shall support dual approval when action can result in serious impact on the industrial process. NOTE Dual approval should be limited to actions which require a very high level of confidence that they will be performed reliably and correctly. Requiring dual approval provides emphasis to the seriousness of consequences that would result from failure of a correct action. An example of a situation in which dual approval is required would be a change to a set point of a critical industrial process. Dual approval mechanisms should not be employed when an immediate response is necessary to safeguard HSE consequences, for example, emergency s hutdown of an industrial process.
6 | 6.3 | FR 2 – Use control | 6.3.4-1 | CR 2.1 – Authorization enforcement | Requirements for the security level that relates to SL-C(UC,component) 1: CR 2.1
6 | 6.3 | FR 2 – Use control | 6.3.4-2 | CR 2.1 – Authorization enforcement | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.1 (1) (2)
6 | 6.3 | FR 2 – Use control | 6.3.4-3 | CR 2.1 – Authorization enforcement | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.1 (1) (2) (3)
6 | 6.3 | FR 2 – Use control | 6.3.4-4 | CR 2.1 – Authorization enforcement | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.1 (1) (2) (3) (4)
6 | 6.4 | FR 2 – Use control | 6.4.1 | CR 2.2 – Wireless use control | If a component supports usage through wireless interfaces it shall provide the capability to integrate into the system that supports usage authorization, monitoring and restrictions according to commonly accepted industry practices.
6 | 6.4 | FR 2 – Use control | 6.4.4-1 | CR 2.2 – Wireless use control | Requirements for the security level that relates to SL-C(UC,component) 1: CR 2.2
6 | 6.4 | FR 2 – Use control | 6.4.4-2 | CR 2.2 – Wireless use control | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.2
6 | 6.4 | FR 2 – Use control | 6.4.4-3 | CR 2.2 – Wireless use control | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.2
6 | 6.4 | FR 2 – Use control | 6.4.4-4 | CR 2.2 – Wireless use control | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.2
6 | 6.5 | FR 2 – Use control |  | CR 2.3 – Use control for portable and mobile devices | There is no component level requirement associated with ISA‑62443‑3‑3 SR 2.3.
6 | 6.6 | FR 2 – Use control |  | CR 2.4 – Mobile code | The use control requirements for mobile code are component-specific and can be located as requirements for each specific component type in Clauses 12 through 15.
6 | 6.7 | FR 2 – Use control | 6.7.1 | CR 2.5 – Session lock | If a component provides a human user interface, whether accessed locally or via a network, the component shall provide the capability a) to protect against further access by initiating a session lock after a configurable time period of inactivity or by manual initiation by the user (human, software process or device); and b) for the session lock to remain in effect until the human user who owns the session, or another authorized human user, re-establishes access using appropriate identification and authentication procedures.
6 | 6.7 | FR 2 – Use control | 6.7.4-1 | CR 2.5 – Session lock | Requirements for the security level that relates to SL-C(UC,component) 1: CR 2.5
6 | 6.7 | FR 2 – Use control | 6.7.4-2 | CR 2.5 – Session lock | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.5
6 | 6.7 | FR 2 – Use control | 6.7.4-3 | CR 2.5 – Session lock | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.5
6 | 6.7 | FR 2 – Use control | 6.7.4-4 | CR 2.5 – Session lock | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.5
6 | 6.8 | FR 2 – Use control | 6.8.1 | CR 2.6 – Remote session termination | If a component supports remote sessions, the component shall provide the capability to terminate a remote session either automatically after a configurable time period of inactivity , manually by a local authority, or manually by the user (human, software process or device) who initiated the session.
6 | 6.8 | FR 2 – Use control | 6.8.4-1 | CR 2.6 – Remote session termination | Requirements for the security level that relates to SL-C(UC,component) 1: Not Selected
6 | 6.8 | FR 2 – Use control | 6.8.4-2 | CR 2.6 – Remote session termination | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.6
6 | 6.8 | FR 2 – Use control | 6.8.4-3 | CR 2.6 – Remote session termination | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.6
6 | 6.8 | FR 2 – Use control | 6.8.4-4 | CR 2.6 – Remote session termination | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.6
6 | 6.9 | FR 2 – Use control | 6.9.1 | CR 2.7 – Concurrent session control | Components shall provide the capability to limit the number of concurrent sessions per interface for any given user (human, software process or device).
6 | 6.9 | FR 2 – Use control | 6.9.4-1 | CR 2.7 – Concurrent session control | Requirements for the security level that relates to SL-C(UC,component) 1: Not Selected
6 | 6.9 | FR 2 – Use control | 6.9.4-2 | CR 2.7 – Concurrent session control | Requirements for the security level that relates to SL-C(UC,component) 2: Not Selected
6 | 6.9 | FR 2 – Use control | 6.9.4-3 | CR 2.7 – Concurrent session control | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.7
6 | 6.9 | FR 2 – Use control | 6.9.4-4 | CR 2.7 – Concurrent session control | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.7
6 | 6.10 | FR 2 – Use control | 6.10.1 | CR 2.8 – Auditable events | Components shall provide the capability to generate audit records relevant to securit y for the following categories: a) access control; b) request errors; c) control system events; d) backup and restore event; e) configuration changes; and f) audit log events. Individual audit records shall include: a) timestamp; b) source (originating device, software process or human user account); c) category; d) type; e) event ID; and f) event result.
6 | 6.10 | FR 2 – Use control | 6.10.4-1 | CR 2.8 – Auditable events | Requirements for the security level that relates to SL-C(UC,component) 1: CR 2.8
6 | 6.10 | FR 2 – Use control | 6.10.4-2 | CR 2.8 – Auditable events | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.8
6 | 6.10 | FR 2 – Use control | 6.10.4-3 | CR 2.8 – Auditable events | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.8
6 | 6.10 | FR 2 – Use control | 6.10.4-4 | CR 2.8 – Auditable events | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.8
6 | 6.11 | FR 2 – Use control | 6.11.1 | CR 2.9 – Audit storage capacity | Components shall a) provide the capability to allocate audit record storage capacity according to commonly recognized recommendations for log management; and b) provide mechanisms to protect against a failure of the component when it reaches or exceeds the audit storage capacity
6 | 6.11 | FR 2 – Use control | 6.11.3-1 | CR 2.9 – Audit storage capacity | Components shall provide the capability to issue a warning when the allocated audit record storage reaches a configurable threshold.
6 | 6.11 | FR 2 – Use control | 6.11.4-1 | CR 2.9 – Audit storage capacity | Requirements for the security level that relates to SL-C(UC,component) 1: CR 2.9
6 | 6.11 | FR 2 – Use control | 6.11.4-2 | CR 2.9 – Audit storage capacity | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.9
6 | 6.11 | FR 2 – Use control | 6.11.4-3 | CR 2.9 – Audit storage capacity | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.9 (1)
6 | 6.11 | FR 2 – Use control | 6.11.4-4 | CR 2.9 – Audit storage capacity | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.9 (1)
6 | 6.12 | FR 2 – Use control | 6.12.1 | CR 2.10 – Response to audit processing failures | Components shall a) provide the capability to protect against the loss of essential services and functions in the event of an audit processing failure; and b) provide the capability to support appropriate actions in response to an audit processing failure according to commonly accepted industry practices and recommendations.
6 | 6.12 | FR 2 – Use control | 6.12.4-1 | CR 2.10 – Response to audit processing failures | Requirements for the security level that relates to SL-C(UC,component) 1: CR 2.10
6 | 6.12 | FR 2 – Use control | 6.12.4-2 | CR 2.10 – Response to audit processing failures | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.10
6 | 6.12 | FR 2 – Use control | 6.12.4-3 | CR 2.10 – Response to audit processing failures | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.10
6 | 6.12 | FR 2 – Use control | 6.12.4-4 | CR 2.10 – Response to audit processing failures | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.10
6 | 6.13 | FR 2 – Use control | 6.13.1 | CR 2.11 – Timestamps | Components shall provide the capability to create timestamps (including date and time) for use in audit records.
6 | 6.13 | FR 2 – Use control | 6.13.3-1 | CR 2.11 – Timestamps | Components shall provide the capability to create timestamps that are synchronized with a system wide time source.
6 | 6.13 | FR 2 – Use control | 6.13.3-2 | CR 2.11 – Timestamps | The time synchronization mechanism shall provide the capability to detect unauthorized alteration and cause an audit event upon alteration.
6 | 6.13 | FR 2 – Use control | 6.13.4-1 | CR 2.11 – Timestamps | Requirements for the security level that relates to SL-C(UC,component) 1: CR 2.11
6 | 6.13 | FR 2 – Use control | 6.13.4-2 | CR 2.11 – Timestamps | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.11 (1)
6 | 6.13 | FR 2 – Use control | 6.13.4-3 | CR 2.11 – Timestamps | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.11 (1)
6 | 6.13 | FR 2 – Use control | 6.13.4-4 | CR 2.11 – Timestamps | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.11 (1) (2)
6 | 6.14 | FR 2 – Use control | 6.14.1 | CR 2.12 – Non-repudiation | If a component provides a human user interface, the component shall provide the capability to determine whether a given human user took a particular action. Control elements that are not able to support such capability shall be l isted in component documents.
6 | 6.14 | FR 2 – Use control | 6.14.3-1 | CR 2.12 – Non-repudiation | Components shall provide the capability to determine whether a given user (human, software process or device) took a particular action.
6 | 6.14 | FR 2 – Use control | 6.14.4-1 | CR 2.12 – Non-repudiation | Requirements for the security level that relates to SL-C(UC,component) 1: CR 2.12
6 | 6.14 | FR 2 – Use control | 6.14.4-2 | CR 2.12 – Non-repudiation | Requirements for the security level that relates to SL-C(UC,component) 2: CR 2.12
6 | 6.14 | FR 2 – Use control | 6.14.4-3 | CR 2.12 – Non-repudiation | Requirements for the security level that relates to SL-C(UC,component) 3: CR 2.12
6 | 6.14 | FR 2 – Use control | 6.14.4-4 | CR 2.12 – Non-repudiation | Requirements for the security level that relates to SL-C(UC,component) 4: CR 2.12 (1)
6 | 6.15 | FR 2 – Use control |  | CR 2.13 – Use of physical diagnostic and test interfaces | The use of physical diagnostic and test interfaces requirements are component-specific and can be located as requirements for each specific component type in Clauses 12 through 15.
7 | 7.1 | FR 3 – System integrity | 7.1-SL 1 | Purpose and SL-C(SI) descriptions | Protect the integrity of the IACS against casual or coincidental manipulation
7 | 7.1 | FR 3 – System integrity | 7.1-SL 2 | Purpose and SL-C(SI) descriptions | Protect the integrity of the IACS against manipulation by someone using simple means with low resources, generic skills and low motivation.
7 | 7.1 | FR 3 – System integrity | 7.1-SL 3 | Purpose and SL-C(SI) descriptions | Protect the integrity of the IACS against manipulation by someone using sophisticated means with moderate resources, IACS specific skills and moderate motivation.
7 | 7.1 | FR 3 – System integrity | 7.1-SL 4 | Purpose and SL-C(SI) descriptions | Protect the integrity of the IACS against manipulation by someone using sophisticated means with extended resources, IACS specific skills and high motivation.
7 | 7.3 | FR 3 – System integrity | 7.3.1 | CR 3.1 – Communication integrity | Components shall provide the capability to protect integrity of transmitted information.
7 | 7.3 | FR 3 – System integrity | 7.3.3-1 | CR 3.1 – Communication integrity | Components shall provide the capability to verify the authenticity of received information during communication. NOTE: Both Integrity protection and authentication of origin can be achieved without providing confidentiality protection.
7 | 7.3 | FR 3 – System integrity | 7.3.4-1 | CR 3.1 – Communication integrity | Requirements for the security level that relates to SL-C(SI,component) 1: CR 3.1
7 | 7.3 | FR 3 – System integrity | 7.3.4-2 | CR 3.1 – Communication integrity | Requirements for the security level that relates to SL-C(SI,component) 2: CR 3.1 (1)
7 | 7.3 | FR 3 – System integrity | 7.3.4-3 | CR 3.1 – Communication integrity | Requirements for the security level that relates to SL-C(SI,component) 3: CR 3.1 (1)
7 | 7.3 | FR 3 – System integrity | 7.3.4-4 | CR 3.1 – Communication integrity | Requirements for the security level that relates to SL-C(SI,component) 4: CR 3.1 (1)
7 | 7.4 | FR 3 – System integrity |  | CR 3.2 – Protection from malicious code | The protection from malicious code requirements are component-specific and can be located as requirements for each specific component type in Clauses 12 through 15.
7 | 7.5 | FR 3 – System integrity | 7.5.1 | CR 3.3 – Security functionality verification | Components shall provide the capability to support verification of the intended operation of security functions according to ISA‑62443‑3‑3 [11] SR3.3.
7 | 7.5 | FR 3 – System integrity | 7.5.3-1 | CR 3.3 – Security functionality verification | Components shall provide the capability to support verification of the intended operation of security functions during normal operations. NOTE This RE needs to be carefully implemented to avoid detrimental effects. It may not be suitable for safety systems.
7 | 7.5 | FR 3 – System integrity | 7.5.4-1 | CR 3.3 – Security functionality verification | Requirements for the security level that relates to SL-C(SI,component) 1: CR 3.3
7 | 7.5 | FR 3 – System integrity | 7.5.4-2 | CR 3.3 – Security functionality verification | Requirements for the security level that relates to SL-C(SI,component) 2: CR 3.3
7 | 7.5 | FR 3 – System integrity | 7.5.4-3 | CR 3.3 – Security functionality verification | Requirements for the security level that relates to SL-C(SI,component) 3: CR 3.3
7 | 7.5 | FR 3 – System integrity | 7.5.4-4 | CR 3.3 – Security functionality verification | Requirements for the security level that relates to SL-C(SI,component) 4: CR 3.3 (1)
7 | 7.6 | FR 3 – System integrity | 7.6.1 | CR 3.4 – Software and information integrity | Components shall provide the capability to perform or support integrity checks on software, configuration and other information as well as the recording and reporting of the results of these checks or be integrated into a system that can perform or support integrity checks.
7 | 7.6 | FR 3 – System integrity | 7.6.3-1 | CR 3.4 – Software and information integrity | Components shall provide the capability to perform or support authenticity checks on software, configuration and other information as well as the recording and reporting of the results of these checks or be integrated into a system that can perform or support authenticity checks.
7 | 7.6 | FR 3 – System integrity | 7.6.3-2 | CR 3.4 – Software and information integrity | If the component is performing the integrity check, it shall be capable of automatically providing notification to a configurable entity upon discovery of an attempt to make an unauthorized change.
7 | 7.6 | FR 3 – System integrity | 7.6.4-1 | CR 3.4 – Software and information integrity | Requirements for the security level that relates to SL-C(SI,component) 1: CR 3.4
7 | 7.6 | FR 3 – System integrity | 7.6.4-2 | CR 3.4 – Software and information integrity | Requirements for the security level that relates to SL-C(SI,component) 2: CR 3.4 (1)
7 | 7.6 | FR 3 – System integrity | 7.6.4-3 | CR 3.4 – Software and information integrity | Requirements for the security level that relates to SL-C(SI,component) 3: CR 3.4 (1) (2)
7 | 7.6 | FR 3 – System integrity | 7.6.4-4 | CR 3.4 – Software and information integrity | Requirements for the security level that relates to SL-C(SI,component) 4: CR 3.4 (1) (2)
7 | 7.7 | FR 3 – System integrity | 7.7.1 | CR 3.5 – Input validation | Components shall validate the syntax, length and content of any input data that is used as an industrial process control input or input via external interfaces that directly impacts the action of the component.
7 | 7.7 | FR 3 – System integrity | 7.7.4-1 | CR 3.5 – Input validation | Requirements for the security level that relates to SL-C(SI,component) 1: CR 3.5
7 | 7.7 | FR 3 – System integrity | 7.7.4-2 | CR 3.5 – Input validation | Requirements for the security level that relates to SL-C(SI,component) 2: CR 3.5
7 | 7.7 | FR 3 – System integrity | 7.7.4-3 | CR 3.5 – Input validation | Requirements for the security level that relates to SL-C(SI,component) 3: CR 3.5
7 | 7.7 | FR 3 – System integrity | 7.7.4-4 | CR 3.5 – Input validation | Requirements for the security level that relates to SL-C(SI,component) 4: CR 3.5
7 | 7.8 | FR 3 – System integrity | 7.8.1 | CR 3.6 – Deterministic output | Components that physically or logically connect to an automation process shall provide the capability to set outputs to a predetermined state if normal operation as defined by the component supplier cannot be maintained.
7 | 7.8 | FR 3 – System integrity | 7.8.4-1 | CR 3.6 – Deterministic output | Requirements for the security level that relates to SL-C(SI,component) 1: CR 3.6
7 | 7.8 | FR 3 – System integrity | 7.8.4-2 | CR 3.6 – Deterministic output | Requirements for the security level that relates to SL-C(SI,component) 2: CR 3.6
7 | 7.8 | FR 3 – System integrity | 7.8.4-3 | CR 3.6 – Deterministic output | Requirements for the security level that relates to SL-C(SI,component) 3: CR 3.6
7 | 7.8 | FR 3 – System integrity | 7.8.4-4 | CR 3.6 – Deterministic output | Requirements for the security level that relates to SL-C(SI,component) 4: CR 3.6
7 | 7.9 | FR 3 – System integrity | 7.9.1 | CR 3.7 – Error handling | Components shall identify and handle error conditions in a manner that does not provide information that could be exploited by adversaries to attack the IACS.
7 | 7.9 | FR 3 – System integrity | 7.9.4-1 | CR 3.7 – Error handling | Requirements for the security level that relates to SL-C(SI,component) 1: CR 3.7
7 | 7.9 | FR 3 – System integrity | 7.9.4-2 | CR 3.7 – Error handling | Requirements for the security level that relates to SL-C(SI,component) 2: CR 3.7
7 | 7.9 | FR 3 – System integrity | 7.9.4-3 | CR 3.7 – Error handling | Requirements for the security level that relates to SL-C(SI,component) 3: CR 3.7
7 | 7.9 | FR 3 – System integrity | 7.9.4-4 | CR 3.7 – Error handling | Requirements for the security level that relates to SL-C(SI,component) 4: CR 3.7
7 | 7.10 | FR 3 – System integrity | 7.10.1 | CR 3.8 – Session integrity | Components shall provide mechanisms to protect the integrity of communications sessions including: a) the capability to invalidate session identifiers upon user logout or other session termination (including browser sessions); b) the capability to generate a unique session identifier for each session and recognize only session identifiers that are system-generated; and c) the capability to generate unique session identifiers with commonly accepted sources of randomness.
7 | 7.10 | FR 3 – System integrity | 7.10.4-1 | CR 3.8 – Session integrity | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
7 | 7.10 | FR 3 – System integrity | 7.10.4-2 | CR 3.8 – Session integrity | Requirements for the security level that relates to SL-C(SI,component) 2: CR 3.8
7 | 7.10 | FR 3 – System integrity | 7.10.4-3 | CR 3.8 – Session integrity | Requirements for the security level that relates to SL-C(SI,component) 3: CR 3.8
7 | 7.10 | FR 3 – System integrity | 7.10.4-4 | CR 3.8 – Session integrity | Requirements for the security level that relates to SL-C(SI,component) 4: CR 3.8
7 | 7.11 | FR 3 – System integrity | 7.11.1 | CR 3.9 – Protection of audit information | Components shall protect audit information, audit logs, and audit tools (if present) from unauthorized access, modification and deletion.
7 | 7.11 | FR 3 – System integrity | 7.11.3-1 | CR 3.9 – Protection of audit information | Components shall provide the capability to store audit records on hardware-enforced writeonce media.
7 | 7.11 | FR 3 – System integrity | 7.11.4-1 | CR 3.9 – Protection of audit information | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
7 | 7.11 | FR 3 – System integrity | 7.11.4-2 | CR 3.9 – Protection of audit information | Requirements for the security level that relates to SL-C(SI,component) 2: CR 3.9
7 | 7.11 | FR 3 – System integrity | 7.11.4-3 | CR 3.9 – Protection of audit information | Requirements for the security level that relates to SL-C(SI,component) 3: CR 3.9
7 | 7.11 | FR 3 – System integrity | 7.11.4-4 | CR 3.9 – Protection of audit information | Requirements for the security level that relates to SL-C(SI,component) 4: CR 3.9 (1)
7 | 7.12 | FR 3 – System integrity |  | CR 3.10 – Support for updates | The support for updates requirements are component-specific and can be located as requirements for each specific device type in Clauses 12 through 15.
7 | 7.13 | FR 3 – System integrity |  | CR 3.11 – Physical tamper resistance and detection | The physical tamper resistance and detection requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15.
7 | 7.14 | FR 3 – System integrity |  | CR 3.12 – Provisioning product supplier roots of trust | The provisioning product supplier roots of trust requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15.
7 | 7.15 | FR 3 – System integrity |  | CR 3.13 – Provisioning asset owner roots of trust | The provisioning asset owner roots of trust requirements are component -specific and can be located as requirements for each specific device type in Clauses 12 through 15.
7 | 7.16 | FR 3 – System integrity |  | CR 3.14 – Integrity of the boot process | The integrity of the boot process requirements are component-specific and can be located as requirements for each specific device type in Clauses 12 through 15
8 | 8.1 | FR 4 – Data confidentiality | 8.1-SL 1 | Purpose and SL-C(DC) descriptions | Prevent the unauthorized disclosure of information via eavesdropping or casual exposure.
8 | 8.1 | FR 4 – Data confidentiality | 8.1-SL 2 | Purpose and SL-C(DC) descriptions | Prevent the unauthorized disclosure of information to an entity actively searching for it using simple means with low resources, generic skills and low motivation.
8 | 8.1 | FR 4 – Data confidentiality | 8.1-SL 3 | Purpose and SL-C(DC) descriptions | Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with moderate resources, IACS specific skills and moderate motivation.
8 | 8.1 | FR 4 – Data confidentiality | 8.1-SL 4 | Purpose and SL-C(DC) descriptions | Prevent the unauthorized disclosure of information to an entity actively searching for it using sophisticated means with extended resources, IACS specific skills and high motivation.
8 | 8.3 | FR 4 – Data confidentiality | 8.3.1 | CR 4.1 – Information confidentiality | Components shall a) provide the capability to protect the confidentiality of information at rest for which explicit read authorization is supported; and b) support the protection of the confidentiality of information in transit as defined in ISA‑62443‑3‑3 [11] SR 4.1.
8 | 8.3 | FR 4 – Data confidentiality | 8.3.4-1 | CR 4.1 – Information confidentiality | Requirements for the security level that relates to SL-C(DC,component) 1: CR 4.1
8 | 8.3 | FR 4 – Data confidentiality | 8.3.4-2 | CR 4.1 – Information confidentiality | Requirements for the security level that relates to SL-C(DC,component) 2: CR 4.1
8 | 8.3 | FR 4 – Data confidentiality | 8.3.4-3 | CR 4.1 – Information confidentiality | Requirements for the security level that relates to SL-C(DC,component) 3: CR 4.1
8 | 8.3 | FR 4 – Data confidentiality | 8.3.4-4 | CR 4.1 – Information confidentiality | Requirements for the security level that relates to SL-C(DC,component) 4: CR 4.1
8 | 8.4 | FR 4 – Data confidentiality | 8.4.1 | CR 4.2 – Information persistence | Components shall provide the capability to erase all information, for which explicit read authorization is supported, from components to be released from active service and/or decommissioned.
8 | 8.4 | FR 4 – Data confidentiality | 8.4.3-1 | CR 4.2 – Information persistence | Components shall provide the capability to protect against unauthorized and unintended information transfer via volatile shared memory resources. NOTE Volatile memory resources are those that generally do not retain information after being released to memory management. However, there are attacks against random access memory (RAM) which might extract key material or other confidential data before it is actually over-written. Therefore, when volatile shared memory is released back to the control system for use by a different user, all unique data and connections to unique data need to be purged from the resource so it is not visible or accessible to the new user.
8 | 8.4 | FR 4 – Data confidentiality | 8.4.3-2 | CR 4.2 – Information persistence | Components shall provide the capability to verify that the erasure of information occurred.
8 | 8.4 | FR 4 – Data confidentiality | 8.4.4-1 | CR 4.2 – Information persistence | Requirements for the security level that relates to SL-C(DC,component) 1: Not selected
8 | 8.4 | FR 4 – Data confidentiality | 8.4.4-2 | CR 4.2 – Information persistence | Requirements for the security level that relates to SL-C(DC,component) 2: CR 4.2
8 | 8.4 | FR 4 – Data confidentiality | 8.4.4-3 | CR 4.2 – Information persistence | Requirements for the security level that relates to SL-C(DC,component) 3: CR 4.2 (1) (2)
8 | 8.4 | FR 4 – Data confidentiality | 8.4.4-4 | CR 4.2 – Information persistence | Requirements for the security level that relates to SL-C(DC,component) 4: CR 4.2 (1) (2)
8 | 8.5 | FR 4 – Data confidentiality | 8.5.1 | CR 4.3 – Use of cryptography | If cryptography is required, the component shall use cryptographic security mechanisms according to internationally recognized and proven security practices and recommendations.
8 | 8.5 | FR 4 – Data confidentiality | 8.5.4-1 | CR 4.3 – Use of cryptography | Requirements for the security level that relates to SL-C(DC,component) 1: CR 4.3
8 | 8.5 | FR 4 – Data confidentiality | 8.5.4-2 | CR 4.3 – Use of cryptography | Requirements for the security level that relates to SL-C(DC,component) 2: CR 4.3
8 | 8.5 | FR 4 – Data confidentiality | 8.5.4-3 | CR 4.3 – Use of cryptography | Requirements for the security level that relates to SL-C(DC,component) 3: CR 4.3
8 | 8.5 | FR 4 – Data confidentiality | 8.5.4-4 | CR 4.3 – Use of cryptography | Requirements for the security level that relates to SL-C(DC,component) 4: CR 4.3
9 | 9.1 | FR 5 – Restricted data flow | 9.1-SL 1 | Purpose and SL-C(RDF) descriptions | Prevent the casual or coincidental circumvention of zone and conduit segmentation.
9 | 9.1 | FR 5 – Restricted data flow | 9.1-SL 2 | Purpose and SL-C(RDF) descriptions | Prevent the intended circumvention of zone and conduit segmentation by entities using simple means with low resources, generic skills and low motivation.
9 | 9.1 | FR 5 – Restricted data flow | 9.1-SL 3 | Purpose and SL-C(RDF) descriptions | Prevent the intended circumvention of zone and conduit segmentation by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation.
9 | 9.1 | FR 5 – Restricted data flow | 9.1-SL 4 | Purpose and SL-C(RDF) descriptions | Prevent the intended circumvention of zone and conduit segmentation by entities using sophisticated means with extended resources, IACS specific skills and high motivation.
9 | 9.3 | FR 5 – Restricted data flow | 9.3.1 | CR 5.1 – Network segmentation | Components shall support a segmented network to support zones and conduits, as needed, to support the broader network architecture based on logical segmentation and criticality
9 | 9.3 | FR 5 – Restricted data flow | 9.3.4-1 | CR 5.1 – Network segmentation | Requirements for the security level that relates to SL-C(RDF,component) 1: CR 5.1
9 | 9.3 | FR 5 – Restricted data flow | 9.3.4-2 | CR 5.1 – Network segmentation | Requirements for the security level that relates to SL-C(RDF,component) 2: CR 5.1
9 | 9.3 | FR 5 – Restricted data flow | 9.3.4-3 | CR 5.1 – Network segmentation | Requirements for the security level that relates to SL-C(RDF,component) 3: CR 5.1
9 | 9.3 | FR 5 – Restricted data flow | 9.3.4-4 | CR 5.1 – Network segmentation | Requirements for the security level that relates to SL-C(RDF,component) 4: CR 5.1
9 | 9.4 | FR 5 – Restricted data flow |  | CR 5.2 – Zone boundary protection | The zone boundary protection requirements are network-component-specific and can be located as requirements for network devices in Clause 15.
9 | 9.5 | FR 5 – Restricted data flow |  | CR 5.3 – General-purpose person-to-person communication restrictions | The general-purpose person-to-person communication restriction requirements are network - component-specific and can be located as requirements for network devices later in Clause 15.
9 | 9.6 | FR 5 – Restricted data flow |  | CR 5.4 – Application partitioning | There is no component level requirement associated with ISA‑62443‑3‑3 SR 5.4.
10 | 10.1 | FR 6 – Timely response to events | 10.1-SL 1 | Purpose and SL-C(TRE) descriptions | Monitor the operation of the components of the IACS, and respond to incidents when discovered, by collecting and providing the forensic evidence when queried.
10 | 10.1 | FR 6 – Timely response to events | 10.1-SL 2 | Purpose and SL-C(TRE) descriptions | Monitor the operation of the components of the IACS, and respond to incidents when discovered, by actively collecting and periodically reporting forensic evidence.
10 | 10.1 | FR 6 – Timely response to events | 10.1-SL 3 | Purpose and SL-C(TRE) descriptions | Monitor the operation of the components of the IACS, and respond to incidents when discovered, by actively collecting and pushing forensic evidence to the proper authorities.
10 | 10.1 | FR 6 – Timely response to events | 10.1-SL 4 | Purpose and SL-C(TRE) descriptions | Monitor the operation of the components of the IACS, and respond to incidents when discovered, by actively collecting and pushing forensic evidence to the proper authorities in near real-time.
10 | 10.3 | FR 6 – Timely response to events | 10.3.1 | CR 6.1 – Audit log accessibility | Components shall provide the capability for authorized humans and/or tools to access audit logs on a read-only basis.
10 | 10.3 | FR 6 – Timely response to events | 10.3.3-1 | CR 6.1 – Audit log accessibility | Components shall provide programmatic access to audit records by either using an application programming interface (API) or sending the audit records to a centralized system
10 | 10.3 | FR 6 – Timely response to events | 10.3.4-1 | CR 6.1 – Audit log accessibility | Requirements for the security level that relates to SL-C(TRE,component) 1: CR 6.1
10 | 10.3 | FR 6 – Timely response to events | 10.3.4-2 | CR 6.1 – Audit log accessibility | Requirements for the security level that relates to SL-C(TRE,component) 2: CR 6.1
10 | 10.3 | FR 6 – Timely response to events | 10.3.4-3 | CR 6.1 – Audit log accessibility | Requirements for the security level that relates to SL-C(TRE,component) 3: CR 6.1 (1)
10 | 10.3 | FR 6 – Timely response to events | 10.3.4-4 | CR 6.1 – Audit log accessibility | Requirements for the security level that relates to SL-C(TRE,component) 4: CR 6.1 (1)
10 | 10.4 | FR 6 – Timely response to events | 10.4.1 | CR 6.2 – Continuous monitoring | Components shall provide the capability to be continuously monitored using commonly accepted security industry practices and recommendations to detect, characterize and report security breaches in a timely manner.
10 | 10.4 | FR 6 – Timely response to events | 10.4.4-1 | CR 6.2 – Continuous monitoring | Requirements for the security level that relates to SL-C(TRE,component) 1: Not Selected
10 | 10.4 | FR 6 – Timely response to events | 10.4.4-2 | CR 6.2 – Continuous monitoring | Requirements for the security level that relates to SL-C(TRE,component) 2: CR 6.2
10 | 10.4 | FR 6 – Timely response to events | 10.4.4-3 | CR 6.2 – Continuous monitoring | Requirements for the security level that relates to SL-C(TRE,component) 3: CR 6.2
10 | 10.4 | FR 6 – Timely response to events | 10.4.4-4 | CR 6.2 – Continuous monitoring | Requirements for the security level that relates to SL-C(TRE,component) 4: CR 6.2
11 | 11.1 | FR 7 – Resource availability | 11.1-SL 1 | Purpose and SL-C(RA) descriptions | Ensure that the component operates reliably under normal production conditions and prevents denial-of-service situations caused by the casual or coincidental actions of an entity.
11 | 11.1 | FR 7 – Resource availability | 11.1-SL 2 | Purpose and SL-C(RA) descriptions | Ensure that the component operates reliably under normal and abnormal production conditions and prevents denial-of-service situations by entities using simple means with low resources, generic skills and low motivation.
11 | 11.1 | FR 7 – Resource availability | 11.1-SL 3 | Purpose and SL-C(RA) descriptions | Ensure that the component operates reliably under normal, abnormal, and extreme production conditions and prevents denial-of-service situations by entities using sophisticated means with moderate resources, IACS specific skills and moderate motivation.
11 | 11.1 | FR 7 – Resource availability | 11.1-SL 4 | Purpose and SL-C(RA) descriptions | Ensure that the component operates reliably under normal, abnormal, and extreme production conditions and prevents denial-of-service situations by entities using sophisticated means with extended resources, IACS specific skills and high motivation.
11 | 11.3 | FR 7 – Resource availability | 11.3.1 | CR 7.1 – Denial of service protection | Components shall provide the capability to maintain essential functions when operating in a degraded mode as the result of a DoS event.
11 | 11.3 | FR 7 – Resource availability | 11.3.3-1 | CR 7.1 – Denial of service protection | Components shall provide the capability to mitigate the effects of information and/or message flooding types of DoS events.
11 | 11.3 | FR 7 – Resource availability | 11.3.4-1 | CR 7.1 – Denial of service protection | Requirements for the security level that relates to SL-C(RA,component) 1: CR 7.1
11 | 11.3 | FR 7 – Resource availability | 11.3.4-2 | CR 7.1 – Denial of service protection | Requirements for the security level that relates to SL-C(RA,component) 2: CR 7.1 (1)
11 | 11.3 | FR 7 – Resource availability | 11.3.4-3 | CR 7.1 – Denial of service protection | Requirements for the security level that relates to SL-C(RA,component) 3: CR 7.1 (1)
11 | 11.3 | FR 7 – Resource availability | 11.3.4-4 | CR 7.1 – Denial of service protection | Requirements for the security level that relates to SL-C(RA,component) 4: CR 7.1 (1)
11 | 11.4 | FR 7 – Resource availability | 11.4.1 | CR 7.2 – Resource management | Components shall provide the capability to limit the use of resources by security functions to protect against resource exhaustion.
11 | 11.4 | FR 7 – Resource availability | 11.4.4-1 | CR 7.2 – Resource management | Requirements for the security level that relates to SL-C(RA,component) 1: CR 7.2
11 | 11.4 | FR 7 – Resource availability | 11.4.4-2 | CR 7.2 – Resource management | Requirements for the security level that relates to SL-C(RA,component) 2: CR 7.2
11 | 11.4 | FR 7 – Resource availability | 11.4.4-3 | CR 7.2 – Resource management | Requirements for the security level that relates to SL-C(RA,component) 3: CR 7.2
11 | 11.4 | FR 7 – Resource availability | 11.4.4-4 | CR 7.2 – Resource management | Requirements for the security level that relates to SL-C(RA,component) 4: CR 7.2
11 | 11.5 | FR 7 – Resource availability | 11.5.1 | CR 7.3 – Control system backup | Components shall provide the capability to participate in system level backup operations in order to safeguard the component state (user- and system-level information). The backup process shall not affect the normal component operations.
11 | 11.5 | FR 7 – Resource availability | 11.5.3-1 | CR 7.3 – Control system backup | Components shall provide the capability to validate the integrity of backed up information prior to the initiation of a restore of that information.
11 | 11.5 | FR 7 – Resource availability | 11.5.4-1 | CR 7.3 – Control system backup | Requirements for the security level that relates to SL-C(RA,component) 1: CR 7.3
11 | 11.5 | FR 7 – Resource availability | 11.5.4-2 | CR 7.3 – Control system backup | Requirements for the security level that relates to SL-C(RA,component) 2: CR 7.3 (1)
11 | 11.5 | FR 7 – Resource availability | 11.5.4-3 | CR 7.3 – Control system backup | Requirements for the security level that relates to SL-C(RA,component) 3: CR 7.3 (1)
11 | 11.5 | FR 7 – Resource availability | 11.5.4-4 | CR 7.3 – Control system backup | Requirements for the security level that relates to SL-C(RA,component) 4: CR 7.3 (1)
11 | 11.6 | FR 7 – Resource availability | 11.6.1 | CR 7.4 – Control system recovery and reconstitution | Components shall provide the capability to be recovered and reconstituted to a known secure state after a disruption or failure.
11 | 11.6 | FR 7 – Resource availability | 11.6.4-1 | CR 7.4 – Control system recovery and reconstitution | Requirements for the security level that relates to SL-C(RA,component) 1: CR 7.4
11 | 11.6 | FR 7 – Resource availability | 11.6.4-2 | CR 7.4 – Control system recovery and reconstitution | Requirements for the security level that relates to SL-C(RA,component) 2: CR 7.4
11 | 11.6 | FR 7 – Resource availability | 11.6.4-3 | CR 7.4 – Control system recovery and reconstitution | Requirements for the security level that relates to SL-C(RA,component) 3: CR 7.4
11 | 11.6 | FR 7 – Resource availability | 11.6.4-4 | CR 7.4 – Control system recovery and reconstitution | Requirements for the security level that relates to SL-C(RA,component) 4: CR 7.4
11 | 11.7 | FR 7 – Resource availability |  | CR 7.5 - Emergency Power | There is no component level requirement associated with ISA‑62443‑3‑3 SR 7.5.
11 | 11.8 | FR 7 – Resource availability | 11.8.1 | CR 7.6 – Network and security configuration settings | Components shall provide the capability to be configured according to recommended network and security configurations as described in guidelines provided by the control system supplier. The component shall provide an interface to the currently deployed network and securit y configuration settings.
11 | 11.8 | FR 7 – Resource availability | 11.8.3-1 | CR 7.6 – Network and security configuration settings | Components shall provide the capability to generate a report listing the currently deployed security settings in a machine-readable format.
11 | 11.8 | FR 7 – Resource availability | 11.8.4-1 | CR 7.6 – Network and security configuration settings | Requirements for the security level that relates to SL-C(RA,component) 1: CR 7.6
11 | 11.8 | FR 7 – Resource availability | 11.8.4-2 | CR 7.6 – Network and security configuration settings | Requirements for the security level that relates to SL-C(RA,component) 2: CR 7.6
11 | 11.8 | FR 7 – Resource availability | 11.8.4-3 | CR 7.6 – Network and security configuration settings | Requirements for the security level that relates to SL-C(RA,component) 3: CR 7.6 (1)
11 | 11.8 | FR 7 – Resource availability | 11.8.4-4 | CR 7.6 – Network and security configuration settings | Requirements for the security level that relates to SL-C(RA,component) 4: CR 7.6 (1)
11 | 11.9 | FR 7 – Resource availability | 11.9.1 | CR 7.7 – Least functionality | Components shall provide the capability to specifically restrict the use of unnecessary functions, ports, protocols and/or services.
11 | 11.9 | FR 7 – Resource availability | 11.9.4-1 | CR 7.7 – Least functionality | Requirements for the security level that relates to SL-C(RA,component) 1: CR 7.7
11 | 11.9 | FR 7 – Resource availability | 11.9.4-2 | CR 7.7 – Least functionality | Requirements for the security level that relates to SL-C(RA,component) 2: CR 7.7
11 | 11.9 | FR 7 – Resource availability | 11.9.4-3 | CR 7.7 – Least functionality | Requirements for the security level that relates to SL-C(RA,component) 3: CR 7.7
11 | 11.9 | FR 7 – Resource availability | 11.9.4-4 | CR 7.7 – Least functionality | Requirements for the security level that relates to SL-C(RA,component) 4: CR 7.7
11 | 11.10 | FR 7 – Resource availability | 11.10.1 | CR 7.8 – Control system component inventory | Components shall provide the capability to support a control system component inventory according to ISA‑62443‑3‑3 [11] SR 7.8.
11 | 11.10 | FR 7 – Resource availability | 11.10.4-1 | CR 7.8 – Control system component inventory | Requirements for the security level that relates to SL-C(RA,component) 1: Not selected
11 | 11.10 | FR 7 – Resource availability | 11.10.4-2 | CR 7.8 – Control system component inventory | Requirements for the security level that relates to SL-C(RA,component) 2: CR 7.8
11 | 11.10 | FR 7 – Resource availability | 11.10.4-3 | CR 7.8 – Control system component inventory | Requirements for the security level that relates to SL-C(RA,component) 3: CR 7.8
11 | 11.10 | FR 7 – Resource availability | 11.10.4-4 | CR 7.8 – Control system component inventory | Requirements for the security level that relates to SL-C(RA,component) 4: CR 7.8
12 | 12.1 | Software application requirements |  | Purpose | The purpose of this set of requirements is to document requirements that are specific to software applications.
12 | 12.2 | Software application requirements | 12.2.1 | SAR 2.4 – Mobile code | In the event that a software application utilizes mobile code technologies, that application shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the software application: a) Control execution of mobile code; b) Control which users (human, software process, or device) are allowed to transfer mobile code to/from the application; c) Control the execution of mobile code based on the results of an integrity check prior to the code being executed.
12 | 12.2 | Software application requirements | 12.3.1-1 | SAR 2.4 – Mobile code | The application shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed.
12 | 12.2 | Software application requirements | 12.2.4-1 | SAR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 1: SAR 2.4
12 | 12.2 | Software application requirements | 12.2.4-2 | SAR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 2: SAR 2.4 (1)
12 | 12.2 | Software application requirements | 12.2.4-3 | SAR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 3: SAR 2.4 (1)
12 | 12.2 | Software application requirements | 12.2.4-4 | SAR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 4: SAR 2.4 (1)
12 | 12.3 | Software application requirements | 12.3.1 | SAR 3.2 – Protection from malicious code | The application product supplier shall qualify and document which protection from malicious code mechanisms are compatible with the application and note any special configuration requirements .
12 | 12.3 | Software application requirements | 12.3.4-1 | SAR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 1: SAR 3.2
12 | 12.3 | Software application requirements | 12.3.4-2 | SAR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 2: SAR 3.2
12 | 12.3 | Software application requirements | 12.3.4-3 | SAR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 3: SAR 3.2
12 | 12.3 | Software application requirements | 12.3.4-4 | SAR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 4: SAR 3.2
13 | 13.1 | Embedded device requirements |  | Purpose | The purpose of this set of requirements is to document requirements that are specific to embedded devices.
13 | 13.2 | Embedded device requirements | 13.2.1 | EDR 2.4 – Mobile code | In the event that an embedded device utilizes mobile code technologies, the embedded device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the embedded device: a) Control execution of mobile code; b) Control which users (human, software process, or device) are allowed to upload mobile code to the device; c) Control the execution of mobile code based on the results of an integrity check prior to the code being executed.
13 | 13.2 | Embedded device requirements | 13.2.3-1 | EDR 2.4 – Mobile code | The embedded device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed
13 | 13.2 | Embedded device requirements | 13.2.4-1 | EDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 1: EDR 2.4
13 | 13.2 | Embedded device requirements | 13.2.4-2 | EDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 2: EDR 2.4 (1)
13 | 13.2 | Embedded device requirements | 13.2.4-3 | EDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 3: EDR 2.4 (1)
13 | 13.2 | Embedded device requirements | 13.2.4-4 | EDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 4: EDR 2.4 (1)
13 | 13.3 | Embedded device requirements | 13.3.1 | EDR 2.13 – Use of physical diagnostic and test interfaces | Embedded devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG Debugging).
13 | 13.3 | Embedded device requirements | 13.3.3-1 | EDR 2.13 – Use of physical diagnostic and test interfaces | Embedded devices shall provide active monitoring of the device’s diagnostic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected.
13 | 13.3 | Embedded device requirements | 13.3.4-1 | EDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
13 | 13.3 | Embedded device requirements | 13.3.4-2 | EDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 2: EDR 2.13
13 | 13.3 | Embedded device requirements | 13.3.4-3 | EDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 3: EDR 2.13 (1)
13 | 13.3 | Embedded device requirements | 13.3.4-4 | EDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 4: EDR 2.13 (1)
13 | 13.4 | Embedded device requirements | 13.4.1 | EDR 3.2 – Protection from malicious code | The embedded device shall provide the capability to protect from installation and execution of unauthorized software.
13 | 13.4 | Embedded device requirements | 13.4.4-1 | EDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 1: EDR 3.2
13 | 13.4 | Embedded device requirements | 13.4.4-2 | EDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 2: EDR 3.2
13 | 13.4 | Embedded device requirements | 13.4.4-3 | EDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 3: EDR 3.2
13 | 13.4 | Embedded device requirements | 13.4.4-4 | EDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 4: EDR 3.2
13 | 13.5 | Embedded device requirements | 13.5.1 | EDR 3.10 – Support for updates | The embedded device shall support the ability to be updated and upgraded.
13 | 13.5 | Embedded device requirements | 13.5.3-1 | EDR 3.10 – Support for updates | The embedded device shall validate the authenticity and integrity of any software update or upgrade prior to installation.
13 | 13.5 | Embedded device requirements | 13.5.4-1 | EDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 1: EDR 3.10
13 | 13.5 | Embedded device requirements | 13.5.4-2 | EDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 2: EDR 3.10 (1)
13 | 13.5 | Embedded device requirements | 13.5.4-3 | EDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 3: EDR 3.10 (1)
13 | 13.5 | Embedded device requirements | 13.5.4-4 | EDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 4: EDR 3.10 (1)
13 | 13.6 | Embedded device requirements | 13.6.1 | EDR 3.11 – Physical tamper resistance and detection | The embedded device shall provide tamper resistance and detection mechanisms to protect against unauthorized physical access into the device
13 | 13.6 | Embedded device requirements | 13.6.3-1 | EDR 3.11 – Physical tamper resistance and detection | The embedded device shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physical access. All notifications of tampering shall be logged as part of the overall audit logging function.
13 | 13.6 | Embedded device requirements | 13.6.4-1 | EDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
13 | 13.6 | Embedded device requirements | 13.6.4-2 | EDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 2: EDR 3.11
13 | 13.6 | Embedded device requirements | 13.6.4-3 | EDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 3: EDR 3.11 (1)
13 | 13.6 | Embedded device requirements | 13.6.4-4 | EDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 4: EDR 3.11 (1)
13 | 13.7 | Embedded device requirements | 13.7.1 | EDR 3.12 – Provisioning product supplier roots of trust | Embedded devices shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roots of trust” at the time of manufacture of the device.
13 | 13.7 | Embedded device requirements | 13.7.4-1 | EDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
13 | 13.7 | Embedded device requirements | 13.7.4-2 | EDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 2: EDR 3.12
13 | 13.7 | Embedded device requirements | 13.7.4-3 | EDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 3: EDR 3.12
13 | 13.7 | Embedded device requirements | 13.7.4-4 | EDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 4: EDR 3.12
13 | 13.8 | Embedded device requirements | 13.8.1 | EDR 3.13 – Provisioning asset owner roots of trust | Embedded devices shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device’s security zone.
13 | 13.8 | Embedded device requirements | 13.8.4-1 | EDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
13 | 13.8 | Embedded device requirements | 13.8.4-2 | EDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 2: EDR 3.13
13 | 13.8 | Embedded device requirements | 13.8.4-3 | EDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 3: EDR 3.13
13 | 13.8 | Embedded device requirements | 13.8.4-4 | EDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 4: EDR 3.13
13 | 13.9 | Embedded device requirements | 13.9.1 | EDR 3.14 – Integrity of the boot process | Embedded devices shall verify the integrity of the firmware, software, and configuration data needed for the component’s boot and runtime processes prior to use.
13 | 13.9 | Embedded device requirements | 13.9.3-1 | EDR 3.14 – Integrity of the boot process | Embedded devices shall use the component’s product supplier roots of trust to verify the authenticity of the firmware, software, and configuration data needed for the component’s boot process prior to it being used in the boot process.
13 | 13.9 | Embedded device requirements | 13.9.4-1 | EDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 1: EDR 3.14
13 | 13.9 | Embedded device requirements | 13.9.4-2 | EDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 2: EDR 3.14 (1)
13 | 13.9 | Embedded device requirements | 13.9.4-3 | EDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 3: EDR 3.14 (1)
13 | 13.9 | Embedded device requirements | 13.9.4-4 | EDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 4: EDR 3.14 (1)
14 | 14.1 | Host device requirements |  | Purpose | The purpose of this set of requirements is to document requirements that are specific to host devices.
14 | 14.2 | Host device requirements | 14.2.1 | HDR 2.4 – Mobile code | In the event that a host device utilizes mobile code technologies, that host device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the host device: a) Control execution of mobile code; b) Control which users (human, software process, or device) are allowed to upload mobile code to the host device; and c) Control the code execution based upon integrity checks on the mobile code and prior to the code being executed.
14 | 14.2 | Host device requirements | 14.2.3-1 | HDR 2.4 – Mobile code | The host device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed.
14 | 14.2 | Host device requirements | 14.2.4-1 | HDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 1: HDR 2.4
14 | 14.2 | Host device requirements | 14.2.4-2 | HDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 2: HDR 2.4 (1)
14 | 14.2 | Host device requirements | 14.2.4-3 | HDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 3: HDR 2.4 (1)
14 | 14.2 | Host device requirements | 14.2.4-4 | HDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 4: HDR 2.4 (1)
14 | 14.3 | Host device requirements | 14.3.1 | HDR 2.13 – Use of physical diagnostic and test interfaces | Host devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG debugging).
14 | 14.3 | Host device requirements | 14.3.3-1 | HDR 2.13 – Use of physical diagnostic and test interfaces | Host devices shall provide active monitoring of the device’s diagnos tic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected.
14 | 14.3 | Host device requirements | 14.3.4-1 | HDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
14 | 14.3 | Host device requirements | 14.3.4-2 | HDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 2: HDR 2.13
14 | 14.3 | Host device requirements | 14.3.4-3 | HDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 3: HDR 2.13 (1)
14 | 14.3 | Host device requirements | 14.3.4-4 | HDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 4: HDR 2.13 (1)
14 | 14.4 | Host device requirements | 14.4.1 | HDR 3.2 – Protection from malicious code | There shall be mechanisms on host devices that are qualified by the IACS product supplier to provide protection from malicious code. The IACS product supplier shall document any special configuration requirements related to protection from malicious code
14 | 14.4 | Host device requirements | 14.4.3-1 | HDR 3.2 – Protection from malicious code | The host device shall automatically report the software and file versions of protection from malicious code in use (as part of overall logging function).
14 | 14.4 | Host device requirements | 14.4.4-1 | HDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 1: HDR 3.2
14 | 14.4 | Host device requirements | 14.4.4-2 | HDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 2: HDR 3.2 (1)
14 | 14.4 | Host device requirements | 14.4.4-3 | HDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 3: HDR 3.2 (1)
14 | 14.4 | Host device requirements | 14.4.4-4 | HDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 4: HDR 3.2 (1)
14 | 14.5 | Host device requirements | 14.5.1 | HDR 3.10 – Support for updates | Host devices shall support the ability to be updated and upgraded.
14 | 14.5 | Host device requirements | 14.5.3-1 | HDR 3.10 – Support for updates | Host devices shall validate the authenticity and integrity of any software update or upgrade prior to installation.
14 | 14.5 | Host device requirements | 14.5.4-1 | HDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 1: HDR 3.10
14 | 14.5 | Host device requirements | 14.5.4-2 | HDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 2: HDR 3.10 (1)
14 | 14.5 | Host device requirements | 14.5.4-3 | HDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 3: HDR 3.10 (1)
14 | 14.5 | Host device requirements | 14.5.4-4 | HDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 4: HDR 3.10 (1)
14 | 14.6 | Host device requirements | 14.6.1 | HDR 3.11 – Physical tamper resistance and detection | Host devices shall provide the capability to support tamper resistance and detection mechanisms to protect against unauthorized physical access into the device.
14 | 14.6 | Host device requirements | 14.6.3-1 | HDR 3.11 – Physical tamper resistance and detection | Host devices shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physical access. All notifications of tampering shall be logged as part of the overall audit logging function.
14 | 14.6 | Host device requirements | 14.6.4-1 | HDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
14 | 14.6 | Host device requirements | 14.6.4-2 | HDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 2: HDR 3.11
14 | 14.6 | Host device requirements | 14.6.4-3 | HDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 3: HDR 3.11 (1)
14 | 14.6 | Host device requirements | 14.6.4-4 | HDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 4: HDR 3.11 (1)
14 | 14.7 | Host device requirements | 14.7.1 | HDR 3.12 – Provisioning product supplier roots of trust | Host devices shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roots of trust” at the time of manufacture of the device.
14 | 14.7 | Host device requirements | 14.7.4-1 | HDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
14 | 14.7 | Host device requirements | 14.7.4-2 | HDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 2: HDR 3.12
14 | 14.7 | Host device requirements | 14.7.4-3 | HDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 3: HDR 3.12
14 | 14.7 | Host device requirements | 14.7.4-4 | HDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 4: HDR 3.12
14 | 14.8 | Host device requirements | 14.8.1 | HDR 3.13 – Provisioning asset owner roots of trust | Host devices shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device’s security zone.
14 | 14.8 | Host device requirements | 14.8.4-1 | HDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 1: Not selected
14 | 14.8 | Host device requirements | 14.8.4-2 | HDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 2: HDR 3.13
14 | 14.8 | Host device requirements | 14.8.4-3 | HDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 3: HDR 3.13
14 | 14.8 | Host device requirements | 14.8.4-4 | HDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 4: HDR 3.13
14 | 14.9 | Host device requirements | 14.9.1 | HDR 3.14 – Integrity of the boot process | Host devices shall verify the integrity of the firmware, software, and configuration data needed for component’s boot process prior to it being used in the boot process.
14 | 14.9 | Host device requirements | 14.9.3-1 | HDR 3.14 – Integrity of the boot process | Host devices shall use the component’s product supplier roots of trust to verify the authenticity of the firmware, software, and configuration data needed for component’s boot process prior to it being used in the boot process.
14 | 14.9 | Host device requirements | 14.9.4-1 | HDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 1: HDR 3.14
14 | 14.9 | Host device requirements | 14.9.4-2 | HDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 2: HDR 3.14 (1)
14 | 14.9 | Host device requirements | 14.9.4-3 | HDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 3: HDR 3.14 (1)
14 | 14.9 | Host device requirements | 14.9.4-4 | HDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 4: HDR 3.14 (1)
14 | 15.1 | Host device requirements |  | Purpose | The purpose of this set of requirements is to document requirements that are specific to network devices.
15 | 15.2 | Network device requirements | 15.2.1 | NDR 1.6 – Wireless access management | A network device supporting wireless access management shall provide the capability to identify and authenticate all users (humans, software processes or devices) engaged in wireless communication.
15 | 15.2 | Network device requirements | 15.2.3-1 | NDR 1.6 – Wireless access management | The network device shall provide the capability to uniquely identify and authenticate all users (humans, software processes or devices) engaged in wireless communication.
15 | 15.2 | Network device requirements | 15.2.4-1 | NDR 1.6 – Wireless access management | Requirements for the security level that relates to SL-C(UC,component) 1: NDR 1.6
15 | 15.2 | Network device requirements | 15.2.4-2 | NDR 1.6 – Wireless access management | Requirements for the security level that relates to SL-C(UC,component) 2: NDR 1.6 (1)
15 | 15.2 | Network device requirements | 15.2.4-3 | NDR 1.6 – Wireless access management | Requirements for the security level that relates to SL-C(UC,component) 3: NDR 1.6 (1)
15 | 15.2 | Network device requirements | 15.2.4-4 | NDR 1.6 – Wireless access management | Requirements for the security level that relates to SL-C(UC,component) 4: NDR 1.6 (1)
15 | 15.3 | Network device requirements | 15.3.1 | NDR 1.13 – Access via untrusted networks | The network device supporting device access into a network shall provide the capability to monitor and control all methods of access to the network device via untrusted networks.
15 | 15.3 | Network device requirements | 15.3.3-1 | NDR 1.13 – Access via untrusted networks | The network device shall provide the capability to deny access requests via untrusted networks unless explicitly approved by an assigned role.
15 | 15.3 | Network device requirements | 15.3.4-1 | NDR 1.13 – Access via untrusted networks | Requirements for the security level that relates to SL-C(UC,component) 1: NDR 1.13
15 | 15.3 | Network device requirements | 15.3.4-2 | NDR 1.13 – Access via untrusted networks | Requirements for the security level that relates to SL-C(UC,component) 2: NDR 1.13
15 | 15.3 | Network device requirements | 15.3.4-3 | NDR 1.13 – Access via untrusted networks | Requirements for the security level that relates to SL-C(UC,component) 3: NDR 1.13 (1)
15 | 15.3 | Network device requirements | 15.3.4-4 | NDR 1.13 – Access via untrusted networks | Requirements for the security level that relates to SL-C(UC,component) 4: NDR 1.13 (1)
15 | 15.4 | Network device requirements | 15.4.1 | NDR 2.4 – Mobile code | In the event that a network device utilizes mobile code technologies, the network device shall provide the capability to enforce a security policy for the usage of mobile code technologies. The security policy shall allow, at a minimum, the following actions for each mobile code technology used on the network device: a) Control execution of mobile code; b) Control which users (human, software process, or device) are allowed to transfer mobile code to/from the network device; and c) Control the code execution based upon integrity checks on mobile code and prior to the code being executed
15 | 15.4 | Network device requirements | 15.4.3-1 | NDR 2.4 – Mobile code | The network device shall provide the capability to enforce a security policy that allows the device to control execution of mobile code based on the results of an authenticity check prior to the code being executed
15 | 15.4 | Network device requirements | 15.4.4-1 | NDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 1: NDR 2.4
15 | 15.4 | Network device requirements | 15.4.4-2 | NDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 2: NDR 2.4 (1)
15 | 15.4 | Network device requirements | 15.4.4-3 | NDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 3: NDR 2.4 (1)
15 | 15.4 | Network device requirements | 15.4.4-4 | NDR 2.4 – Mobile code | Requirements for the security level that relates to SL-C(UC,component) 4: NDR 2.4 (1)
15 | 15.5 | Network device requirements | 15.5.1 | NDR 2.13 – Use of physical diagnostic and test interfaces | Network devices shall protect against unauthorized use of the physical factory diagnostic and test interface(s) (e.g. JTAG debugging).
15 | 15.5 | Network device requirements | 15.5.3-1 | NDR 2.13 – Use of physical diagnostic and test interfaces | Network devices shall provide active monitoring of the device’s diagnostic and test interface(s) and generate an audit log entry when attempts to access these interface(s) are detected.
15 | 15.5 | Network device requirements | 15.5.4-1 | NDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 1: Not Selected
15 | 15.5 | Network device requirements | 15.5.4-2 | NDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 2.13
15 | 15.5 | Network device requirements | 15.5.4-3 | NDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 2.13 (1)
15 | 15.5 | Network device requirements | 15.5.4-4 | NDR 2.13 – Use of physical diagnostic and test interfaces | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 2.13 (1)
15 | 15.6 | Network device requirements | 15.6.1 | NDR 3.2 – Protection from malicious code | The network device shall provide for protection from malicious code.
15 | 15.6 | Network device requirements | 15.6.4-1 | NDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 1: NDR 3.2
15 | 15.6 | Network device requirements | 15.6.4-2 | NDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 3.2
15 | 15.6 | Network device requirements | 15.6.4-3 | NDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 3.2
15 | 15.6 | Network device requirements | 15.6.4-4 | NDR 3.2 – Protection from malicious code | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 3.2
15 | 15.7 | Network device requirements | 15.7.1 | NDR 3.10 – Support for updates | Network devices shall support the ability to be updated and upgraded.
15 | 15.7 | Network device requirements | 15.7.3-1 | NDR 3.10 – Support for updates | Network devices shall validate the authenticity and integrity of any software update or upgrade prior to installation.
15 | 15.7 | Network device requirements | 15.7.4-1 | NDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 1: NDR 3.10
15 | 15.7 | Network device requirements | 15.7.4-2 | NDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 3.10 (1)
15 | 15.7 | Network device requirements | 15.7.4-3 | NDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 3.10 (1)
15 | 15.7 | Network device requirements | 15.7.4-4 | NDR 3.10 – Support for updates | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 3.10 (1)
15 | 15.8 | Network device requirements | 15.8.1 | NDR 3.11 – Physical tamper resistance and detection | Network devices shall provide tamper resistance and detection mechanisms to protect against unauthorized physical access into the device
15 | 15.8 | Network device requirements | 15.8.3-1 | NDR 3.11 – Physical tamper resistance and detection | Network devices shall be capable of automatically providing notification to a configurable set of recipients upon discovery of an attempt to make an unauthorized physical access. All notifications of tampering shall be logged as part of the overall audit logging function.
15 | 15.8 | Network device requirements | 15.8.4-1 | NDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 1: Not Selected
15 | 15.8 | Network device requirements | 15.8.4-2 | NDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 3.11
15 | 15.8 | Network device requirements | 15.8.4-3 | NDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 3.11 (1)
15 | 15.8 | Network device requirements | 15.8.4-4 | NDR 3.11 – Physical tamper resistance and detection | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 3.11 (1)
15 | 15.9 | Network device requirements | 15.9.1 | NDR 3.12 – Provisioning product supplier roots of trust | Network devices shall provide the capability to provision and protect the confidentiality, integrity, and authenticity of product supplier keys and data to be used as one or more “roo ts of trust” at the time of manufacture of the device.
15 | 15.9 | Network device requirements | 15.9.4-1 | NDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 1: Not Selected
15 | 15.9 | Network device requirements | 15.9.4-2 | NDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 3.12
15 | 15.9 | Network device requirements | 15.9.4-3 | NDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 3.12
15 | 15.9 | Network device requirements | 15.9.4-4 | NDR 3.12 – Provisioning product supplier roots of trust | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 3.12
15 | 15.10 | Network device requirements | 15.10.1 | NDR 3.13 – Provisioning asset owner roots of trust | Network devices shall a) provide the capability to provision and protect the confidentiality, integrity, and authenticity of asset owner keys and data to be used as “roots of trust”; and b) support the capability to provision without reliance on components that may be outside of the device’s security zone.
15 | 15.10 | Network device requirements | 15.10.4-1 | NDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 1: Not Selected
15 | 15.10 | Network device requirements | 15.10.4-2 | NDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 3.13
15 | 15.10 | Network device requirements | 15.10.4-3 | NDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 3.13
15 | 15.10 | Network device requirements | 15.10.4-4 | NDR 3.13 – Provisioning asset owner roots of trust | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 3.13
15 | 15.11 | Network device requirements | 15.11.1 | NDR 3.14 – Integrity of the boot process | Network devices shall verify the integrity of the firmware, software, and configuration data needed for component’s boot process prior to it being used in the boot process.
15 | 15.11 | Network device requirements | 15.11.3-1 | NDR 3.14 – Integrity of the boot process | Network devices shall use the component’s product supplier roots of trust to verity the authenticity of the firmware, software, and configuration data needed for component’s boot process prior to it being used in the boot process.
15 | 15.11 | Network device requirements | 15.11.4-1 | NDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 1: NDR 3.14
15 | 15.11 | Network device requirements | 15.11.4-2 | NDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 3.14 (1)
15 | 15.11 | Network device requirements | 15.11.4-3 | NDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 3.14 (1)
15 | 15.11 | Network device requirements | 15.11.4-4 | NDR 3.14 – Integrity of the boot process | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 3.14 (1)
15 | 15.12 | Network device requirements | 15.12.1 | NDR 5.2 – Zone boundary protection | A network device at a zone boundary shall provide the capability to monitor and control communications at zone boundaries to enforce the compartmentalization defined in the risk -based zones and conduits model.
15 | 15.12 | Network device requirements | 15.12.3-1 | NDR 5.2 – Zone boundary protection | The network component shall provide the capability to deny network traffic by default and allow network traffic by exception (also termed deny all, permit by exception).
15 | 15.12 | Network device requirements | 15.12.3-2 | NDR 5.2 – Zone boundary protection | The network component shall provide the capability to protect against any communication through the control system boundary (also termed island mode). NOTE Examples of when this capability may be used include where a security violation and/or breach has been detected within the control system, or an attack is occurring at the enterprise level.
15 | 15.12 | Network device requirements | 15.12.3-3 | NDR 5.2 – Zone boundary protection | The network component shall provide the capability to protect against any communication through the control system boundary when there is an operational failure of the boundary protection mechanisms (also termed fail close). NOTE Examples of when this capability may be used include scenarios where a hardware failure or power failure causes boundary protection devices to function in a degraded mode or fail entirely.
15 | 15.12 | Network device requirements | 15.12.4-1 | NDR 5.2 – Zone boundary protection | Requirements for the security level that relates to SL-C(SI,component) 1: NDR 5.2
15 | 15.12 | Network device requirements | 15.12.4-2 | NDR 5.2 – Zone boundary protection | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 5.2 (1)
15 | 15.12 | Network device requirements | 15.12.4-3 | NDR 5.2 – Zone boundary protection | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 5.2 (1) (2) (3)
15 | 15.12 | Network device requirements | 15.12.4-4 | NDR 5.2 – Zone boundary protection | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 5.2 (1) (2) (3)
15 | 15.13 | Network device requirements | 15.13.1 | NDR 5.3 – General purpose, person-to-person communication restrictions | A network device at a zone boundary shall provide the capability to protect against general purpose, person-to-person messages from being received from users or systems external to the control system.
15 | 15.13 | Network device requirements | 15.13.4-1 | NDR 5.3 – General purpose, person-to-person communication restrictions | Requirements for the security level that relates to SL-C(SI,component) 1: NDR 5.3
15 | 15.13 | Network device requirements | 15.13.4-2 | NDR 5.3 – General purpose, person-to-person communication restrictions | Requirements for the security level that relates to SL-C(SI,component) 2: NDR 5.3
15 | 15.13 | Network device requirements | 15.13.4-3 | NDR 5.3 – General purpose, person-to-person communication restrictions | Requirements for the security level that relates to SL-C(SI,component) 3: NDR 5.3
15 | 15.13 | Network device requirements | 15.13.4-4 | NDR 5.3 – General purpose, person-to-person communication restrictions | Requirements for the security level that relates to SL-C(SI,component) 4: NDR 5.3